BATTERY CHARGING INFO

Bulk Charge:

Whenever the converter is running on nominal AC shore power (and is connected to the batteries), it charges the batteries. During bulk charging, the charger supplies the maximum amount of current to the batteries. The battery voltage rises to a set value (typically 14.1 volts DC for gel-cell batteries: 14.3 volts DC for absorbed glass-mat – AGM – batteries; and 14.6 volts DC for liquid lead acid batteries.

The BULK stage involves about 80% of the recharge, wherein the charger current is held constant (in a constant current charger), and voltage increases. The properly sized charger will give the battery as much current as it will accept up to charger capacity (25% of battery capacity in amp hours), and not raise a wet battery over 125° F, or an AGM or GEL (valve regulated) battery over 100° F.

Absorption Charge:

The ABSORPTION stage (the remaining 20%, approximately) has the charger holding the voltage at the charger's absorption voltage (between 14.1 VDC and 14.8 VDC, depending on charger set points) and decreasing the current until the battery is fully charged. Some charger manufacturers call this absorption stage an equalization stage. We don't agree with this use of the term. If the battery won't hold a charge, or the current does not drop after the expected recharge time, the battery may have some permanent sulphation.

Float Charge:

The batteries are held at the float voltage (typically 13.6 volts DC for gel-cell, 13.1 volts DC for AGM, and 13.4 volts DC for liquid lead acid).

The FLOAT stage is where the charge voltage is reduced to between 13.0 VDC and 13.8 VDC and held constant, while the current is reduced to less than 1% of battery capacity. This mode can be used to maintain a fully charged battery indefinitely

Recharge time can be approximated by dividing the amp hours to be replaced by 90% of the rated output of the charger. For example, a 100 amp hour battery with a 10 % discharge would need 10 amps replaced. Using a 5 amp charger, we have 10 amp hours divided by 90% of 5 amps (.9x5) amps = 2.22 hour recharge time estimate.  A deeply discharged battery deviates from this formula, requiring more time per amp to be replaced.

Recharge frequency recommendations vary from expert to expert. It appears that depth of discharge affects battery life more than frequency of recharge. For example, recharging when the equipment is not going to be used for a while (meal break or whatever), may keep the average depth of discharge above 50% for a service day. This basically applies to battery applications where the average depth of discharge falls below 50% in a day, and the battery can be fully recharged once during a 24 hour period.

### Equalization

Equalization is essentially a controlled over charge. Some charger manufacturers call the peak voltage the charger attains at the end of the BULK mode (absorption voltage) an equalization voltage, but technically it's not. Higher capacity wet (flooded) batteries sometimes benefit from this procedure, particularly the physically tall batteries. The electrolyte in a wet battery can stratify over time, if not cycled occasionally. In equalization, the voltage is brought up above typical peak charging voltage (to 15 to 16 volts in a 12 volt system) well into the gassing stage, and held for a fixed (but limited) period. This stirs up the chemistry in the entire battery, "equalizing" the strength of the electrolyte, and knocking off any loose sulphation that may be on the battery plates.

The construction of AGM and Gel batteries all but eliminates any stratification, and most all manufacturers of this type do not recommend it (advising against it). Some manufacturers (notably Concorde) list a procedure, but voltage and time are critical to avoid battery damage.

### Battery Testing

Battery testing can be done in several ways. The most popular includes measurement of specific gravity, and battery voltage. Specific gravity applies to wet cells with removable caps, giving access to the electrolyte. To measure specific gravity, buy a temperature compensating hydrometer at an auto parts store or tool supply. To measure voltage, use a digital voltmeter in the DC voltage setting. The surface charge must be removed from a freshly charged battery before testing. A 12 hour lapse after charging qualifies, or you may remove the surface charge with a load (20 amps for 3 plus minutes).

Load testing is another method of testing a battery. Load testing removes amps from a battery (similar to starting an engine). Some battery companies label their battery with the amp load for testing. This number is usually 1/2 of the CCA rating. For instance, a 500 CCA battery would load test at 250 amps for 15 seconds. A load test can only be performed if the battery is at or near a full charge. Some electronic load testers apply a 100 amp load for 10 seconds, and then display battery voltage. This number is compared to a chart on the tester, based on CCA rating to determine battery condition.

Sulphation of batteries starts when specific gravity falls below 1.225 or voltage measures less than 12.4 (12v Battery ) or 6.2 (6 volt battery). Sulphation can harden on the battery plates if left long enough, reducing and eventually destroying the ability of the battery to generate rated volts and amps. There are devices for removing hard sulphation, but the best practice is preventing formation by proper battery care and recharging after a discharge cycle. Sulphation is the main reason a significant portion of lead acid batteries don't attain their chemical life span.

# State of Charge		Voltage		Specific Gravity (80F)

# 12Volt		6Volt

100%			12.7		6.3		1.265

75%			12.4		6.2		1.225

50%			12.2		6.1		1.190

25%			12.0		6.0		1.155

Discharged		11.9		6.0		1.120